## Room Sound
Room NC/RC Calculation
Project / Zone: Test print
Duct Width, in. | 15
Duct Height, in. | 15
Lining Thickness, in. | 1
Length Lined duct,Ft | 5
Number of Elbows | 0
Type | 1 | 1, Lined Rectangular | [10 empty] | p/a | 3.2
Number of Tees | 0
Type | 1 | 1, Lined Rectangular
Number of Zones fed | 3
End Reflection, Width, in. | 10
Flex Length, ft. | 5
Diameter, in. | 8
Room Volume, CuFt | 2400
Distance, ft. | 5
Octave Band | 2 | 3 | 4 | 5 | 6 | 7
Mid Frequency, Hz | 125 | 250 | 500 | 1000 | 2000 | 4000 | NC | RC | R? | H? | dBA | Comments
Run 1 | 57 | 55 | 51 | 49 | 40 | 30 | 47.78 | 46.6667 | N | N | 53.2239
Run 2 | [6 empty] | 3.1 | 0 | N | H | 6.2515
Run 3 | [6 empty] | 3.1 | 0 | N | H | 6.2515
Run 4 | [6 empty] | 3.1 | 0 | N | H | 6.2515

## Constants
Sound Constants - ARI 885 -90 and -98
| Band Constants | [6 empty] | Equation
Octave Band | 2 | 3 | 4 | 5 | 6 | 7
Mid Frequency, Hz | 125 | 250 | 500 | 1000 | 2000 | 4000
NC Drivers | [7 empty] | NC= M1*Band Spl+ Intcpt
Intcpt | -31.6 | -18.9 | -8.5 | -2.2 | 1 | 3.1
M1 | 1.28 | 1.18 | 1.09 | 1.02 | 1 | 0.98
Lined Duct
Constants | 125 | 250 | 500 | 1000 | 2000 | 4000 |  | dB/ft = 10^C1 * p/a^C2 * t^C3
C1 | -0.865 | -0.582 | -0.0121 | 0.298 | 0.089 | 0.0649 |  | where :
C2 | 0.723 | 0.826 | 0.487 | 0.513 | 0.862 | 0.629 |  | p/a = 2*(Width+Height)/(Width*Height)*12, in inches |  | Application Reductions
C3 | 0.375 | 0.975 | 0.868 | 0.317 | 0 | 0 |  | t = lining thickness, in. |  | 0 | 0 | 0 | 0 | 0 | 0
Flex Duct
Constants | 125 | 250 | 500 | 1000 | 2000 | 4000 |  | IL, by Band = (C1+C2*Dia+C3*Dia^2) + ((C4+C5*Dia+C6*Dia^2)*Length)
C1 | 3.6011 | -2.0231 | 1.5331 | 24.452 | 26.1549 | 25.06 |  | Diameter in inches, Length in feet
C2 | -0.12506 | 1.2762 | 1.4076 | -2.8449 | -2.8852 | -4.0431
C3 | -0.0063392 | -0.082116 | -0.083166 | 0.085175 | 0.088421 | 0.16269
C4 | 0.48524 | -0.69143 | 1.9482 | 0.83804 | 1.7025 | 0.22397
C5 | 0.075787 | 0.43784 | 0.062717 | 0.3255 | 0.16157 | 0.34437
C6 | -0.0052214 | -0.020816 | -0.0050562 | -0.014685 | -0.0099562 | -0.020039
Elbows, 11-20 " Wide (use Avg = 15")
Elbow Type | 125 | 250 | 500 | 1000 | 2000 | 4000
kHz* avg. width | 1.875 | 3.75 | 7.5 | 15 | 30 | 60
1, Lined Rectangular | 1 | 6 | 6 | 11 | 10 | 10 |  | Excerpted from tables D11,12, ARI 885-98
2, Lined rect, Turning Vanes | 1 | 4 | 4 | 7 | 7 | 7 |  | Using tables below, and freq (in Khz) * Width, the followong tables apply
3, Unlined Rectangular | 1 | 5 | 5 | 8 | 4 | 3
4, Unlined Round | 1 | 2 | 2 | 3 | 3 | 3
Basis of table | Type 1 |  | Type 2 |  | Type 3 |  | Type 4 |  | Hz at 15" width (mean)
Hz | Loss | fw | Loss | fw | Loss | fw | Loss | fw | Loss from ARI 885-98
125 | 1 | 1.9-3.8 | 1 | 1.9-3.8 | 1 | 1.9-3.8 | 1 | 1.9-3.8
250 | 6 | 3.8-7.5 | 4 | 3.8-7.5 | 5 | 3.8-7.5 | 2 | 3.8-7.5
500 | 11 | 7.5 - 15 | 7 | >15 | 8 | 7.5 - 15 | 3 | >7.5
1000 | 10 | >15 |  |  | 4 | 15-30
2000 |  |  |  |  | 3 | >30
Tees, 11-20 " Wide | [7 empty] | Same as above, plus 3db for I split
Elbow Type | 125 | 250 | 500 | 1000 | 2000 | 4000
1, Lined Rectangular | 4 | 9 | 9 | 14 | 13 | 13
2, Lined rect, Turning Vanes | 4 | 7 | 7 | 10 | 10 | 10
3, Unlined Rectangular | 4 | 8 | 8 | 11 | 7 | 6
4, Unlined Round | 4 | 5 | 5 | 6 | 6 | 6
End Reflection | C1 | 1150 | [5 empty] | ERL = 10*LOG(1+(C1/(4*Pi* f ))^2 * (2*Pi/area)) : Area = Sq.Ft.= 0.00545*d^2
| Pi | 3.1416 | [5 empty] | Where F = octave band frequency.
ARI 885-98 / Radiated, combined ceiling plenum/space effect
Ceiling/Plenum Effect Attenuation Values, Radiated sound | [7 empty] | Table from ARI standard
Tile Type | 125 | 250 | 500 | 1000 | 2000 | 4000
1, Mineral Fiber | 16 | 18 | 20 | 26 | 31 | 36
2, Mineral Fiber | 15 | 17 | 19 | 25 | 30 | 33
3, Glass Fiber | 16 | 15 | 17 | 17 | 18 | 19
4, Glass Fiber | 17 | 18 | 21 | 25 | 29 | 35
5, Glass Fiber, TL Backed | 17 | 18 | 22 | 27 | 32 | 39
6, Gypsym Board Tiles | 16 | 18 | 18 | 21 | 22 | 22
7, Solid Gypsum Board | 21 | 25 | 25 | 27 | 27 | 28
8, Solid Gypsum Board | 23 | 27 | 27 | 29 | 29 | 30
9, Double Gypsum Board | 27 | 31 | 31 | 33 | 33 | 34
10, Double Gypsum Board | 29 | 33 | 33 | 35 | 35 | 36
11, Concealed Spline | 23 | 24 | 24 | 29 | 33 | 34
ARI 885-90 / ceiling plenum effect
Ceiling/Plenum Effect Attenuation Values, Radiated sound | [7 empty] | Add to space effect for ARI 885-90 calculations
Tile Type | 125 | 250 | 500 | 1000 | 2000 | 4000
1, Mineral Fiber | 9 | 10 | 12 | 14 | 15 | 15
2, Glass Fiber | 8 | 8 | 8 | 10 | 10 | 14
3, Solid Gypsum Board | 15 | 21 | 25 | 27 | 26 | 27
Space Effect, Point Source | [7 empty] | Shultz equation
Log Distance, ft. | 10 | [6 empty] | Room SPL = Sound Power less (10 * Log(Distance) + 5 * Log(Volume)+ 3 * Log(Freq[I]) - 25)
Log Room Volume, CuFt | 5
Log Frequency, Hz | 3
Constant | 25
Environmental Adjustment Factor
Standard referenced | 125 | 250 | 500 | 1000 | 2000 | 4000
ARI 885-90 | 3 | 2 | 1 | 1 | 1 | 1
ARI 885-98 | 2 | 1 | 0 | 0 | 0 | 0

## NC_Source
WRITTEN BY: TARSHA L. SIMON |  |  |  |  | DATE: Jan 17, 1991
MODIFIED BY: D Int-Hout, 2/95
NCPLOT |  |  |  |  | RC Data
|  | -2 |  |  | 50
|  | -1 |  |  | 45
| 32 | 0 |  | 0 | 40
NC15 | 63 | 1 | 47 | 1 | 35
| 125 | 2 | 36 | 2 | 30
| 250 | 3 | 29 | 3 | 25
| 500 | 4 | 22 | 4 | 20
| 1000 | 5 | 17 | 5 | 15
| 2000 | 6 | 14 | 6 | 10
| 4000 | 7 | 12 | 7 | 5
|  | 8 |  |  | 0
|  | -1 |  |  | 50
| 32 | 0 |  |  | 45
NC20 | 63 | 1 | 51 |  | 40
| 125 | 2 | 40 |  | 35
| 250 | 3 | 33 |  | 30
| 500 | 4 | 26 |  | 25
| 1000 | 5 | 22 |  | 20
| 2000 | 6 | 19 |  | 15
| 4000 | 7 | 17 |  | 10
|  | 8 |  |  | 5
|  | -1 |  |  | 55
| 32 | 0 |  |  | 50
NC25 | 63 | 1 | 54 |  | 45
| 125 | 2 | 44 |  | 40
| 250 | 3 | 37 |  | 35
| 500 | 4 | 31 |  | 30
| 1000 | 5 | 27 |  | 25
| 2000 | 6 | 24 |  | 20
| 4000 | 7 | 22 |  | 15
|  | 8 |  |  | 10
|  | -1 |  |  | 60
|  | 0 |  |  | 55
NC30 | 63 | 1 | 57 |  | 50
| 125 | 2 | 48 |  | 45
| 250 | 3 | 41 |  | 40
| 500 | 4 | 35 |  | 35
| 1000 | 5 | 31 |  | 30
| 2000 | 6 | 29 |  | 25
| 4000 | 7 | 28 |  | 20
|  | 8 |  |  | 15
|  | -1 |  |  | 65
|  | 0 |  |  | 60
NC35 | 63 | 1 | 60 |  | 55
| 125 | 2 | 52 |  | 50
| 250 | 3 | 45 |  | 45
| 500 | 4 | 40 |  | 40
| 1000 | 5 | 36 |  | 35
| 2000 | 6 | 34 |  | 30
| 4000 | 7 | 33 |  | 25
|  | 8 |  |  | 20
|  | -1 |  |  | 70
|  | 0 |  |  | 65
NC40 | 63 | 1 | 64 |  | 60
| 125 | 2 | 56 |  | 55
| 250 | 3 | 50 |  | 50
| 500 | 4 | 45 |  | 45
| 1000 | 5 | 41 |  | 40
| 2000 | 6 | 39 |  | 35
| 4000 | 7 | 38 |  | 30
|  | 8 |  |  | 25
|  | -1 |  |  | 75
|  | 0 |  |  | 70
NC45 | 63 | 1 | 67 |  | 65
| 125 | 2 | 60 |  | 60
| 250 | 3 | 54 |  | 55
| 500 | 4 | 49 |  | 50
| 1000 | 5 | 46 |  | 45
| 2000 | 6 | 44 |  | 40
| 4000 | 7 | 43 |  | 35
|  | 8 |  |  | 30
|  | -1 |  |  | 80
|  | 0 |  |  | 75
NC50 | 63 | 1 | 71 |  | 70
| 125 | 2 | 64 |  | 65
| 250 | 3 | 58 |  | 60
| 500 | 4 | 54 |  | 55
| 1000 | 5 | 51 |  | 50
| 2000 | 6 | 49 |  | 45
| 4000 | 7 | 48 |  | 40
|  | 8 |  |  | 35
|  | -1 |  |  | 85
|  | 0 |  |  | 80
NC55 | 63 | 1 | 74 |  | 75
| 125 | 2 | 67 |  | 70
| 250 | 3 | 62 |  | 65
| 500 | 4 | 58 |  | 60
| 1000 | 5 | 56 |  | 55
| 2000 | 6 | 54 |  | 50
| 4000 | 7 | 53 |  | 45
|  | 8 |  |  | 40
|  | -1 |  |  | 90
|  | 0 |  |  | 85
NC60 | 63 | 1 | 77 |  | 80
| 125 | 2 | 71 |  | 75
| 250 | 3 | 67 |  | 70
| 500 | 4 | 63 |  | 65
| 1000 | 5 | 61 |  | 60
| 2000 | 6 | 59 |  | 55
| 4000 | 7 | 58 |  | 50
|  | 8 |  |  | 45
|  | -1 |  |  | 95
|  | 0 |  |  | 90
NC65 | 63 | 1 | 80 |  | 85
| 125 | 2 | 75 |  | 80
| 250 | 3 | 71 |  | 75
| 500 | 4 | 68 |  | 70
| 1000 | 5 | 66 |  | 65
| 2000 | 6 | 64 |  | 60
| 4000 | 7 | 63 |  | 55
|  | 8 |  |  | 50
|  | -1 | 78 |  | 78
|  | 0 | 58 |  | 58
HEARING THRESHOLD |  | 1 | 36 |  | 36
|  | 2 | 22 |  | 22
|  | 3 | 13 |  | 13
|  | 4 | 8 |  | 1
5
6
7
8

## DbA (1) Calc
Linear, dBA, and dBC Calculations:
June 15, 1995 Version |  |  |  |  | Input O.B. Data Given
Data | Linear | dBA | dBC | No. | Under Linear Column
Freq., Hz. | Input | Calc. | Calc. | Freq., Hz.
31.5 |  | #VALUE! | #VALUE! | 31.5 | Excluded, DIH 10/15/03
63 |  | #VALUE! | #VALUE! | 63
125 | 57 | 40.9 | 56.8 | 125
250 | 55 | 46.4 | 55 | 250
500 | 51 | 47.8 | 51 | 500
1000 | 49 | 49 | 49 | 1000
2000 | 40 | 41.2 | 39.8 | 2000
4000 | 30 | 31 | 29.2 | 4000
8000 |  | #VALUE! | #VALUE! | 8000 | Excluded, DIH 10/15/03
16000 |  | #VALUE! | #VALUE! | 16000
Linear | #VALUE! | - | - | Linear
dBA | - | 53.2239 | - | dBA
dBC | - | - | #VALUE! | dBC
A-wgt | Linear | dBA | dBC | C-wgt
-39.4 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-26.2 |  | #VALUE! | #VALUE! | -0.8
-16.1 | 57 | 40.9 | 56.8 | -0.2
-8.6 | 55 | 46.4 | 55 | 0
-3.2 | 51 | 47.8 | 51 | 0
0 | 49 | 49 | 49 | 0
1.2 | 40 | 41.2 | 39.8 | -0.2
1 | 30 | 31 | 29.2 | -0.8
-1.1 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-6.6 |  | #VALUE! | #VALUE! | -8.5
Overall | #VALUE! | 53.2239 | #VALUE! | Overall
Value | Linear | dBA | dBC | Value

## DbA Calc (2)
Linear, dBA, and dBC Calculations:
June 15, 1995 Version |  |  |  |  | Input O.B. Data Given
Data | Linear | dBA | dBC | No. | Under Linear Column
Freq., Hz. | Input | Calc. | Calc. | Freq., Hz.
31.5 |  | #VALUE! | #VALUE! | 31.5 | Excluded, DIH 10/15/03
63 |  | #VALUE! | #VALUE! | 63
125 | 0 | -16.1 | -0.2 | 125
250 | 0 | -8.6 | 0 | 250
500 | 0 | -3.2 | 0 | 500
1000 | 0 | 0 | 0 | 1000
2000 | 0 | 1.2 | -0.2 | 2000
4000 | 0 | 1 | -0.8 | 4000
8000 |  | #VALUE! | #VALUE! | 8000 | Excluded, DIH 10/15/03
16000 |  | -6.6 | -8.5 | 16000
Linear | #VALUE! | - | - | Linear
dBA | - | 6.2515 | - | dBA
dBC | - | - | #VALUE! | dBC
A-wgt | Linear | dBA | dBC | C-wgt
-39.4 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-26.2 |  | #VALUE! | #VALUE! | -0.8
-16.1 | 0 | -16.1 | -0.2 | -0.2
-8.6 | 0 | -8.6 | 0 | 0
-3.2 | 0 | -3.2 | 0 | 0
0 | 0 | 0 | 0 | 0
1.2 | 0 | 1.2 | -0.2 | -0.2
1 | 0 | 1 | -0.8 | -0.8
-1.1 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-6.6 | 0 | -6.6 | -8.5 | -8.5
Overall | #VALUE! | 6.2515 | #VALUE! | Overall
Value | Linear | dBA | dBC | Value

## DbA Calc (3)
Linear, dBA, and dBC Calculations:
June 15, 1995 Version |  |  |  |  | Input O.B. Data Given
Data | Linear | dBA | dBC | No. | Under Linear Column
Freq., Hz. | Input | Calc. | Calc. | Freq., Hz.
31.5 |  | #VALUE! | #VALUE! | 31.5 | Excluded, DIH 10/15/03
63 |  | #VALUE! | #VALUE! | 63
125 | 0 | -16.1 | -0.2 | 125
250 | 0 | -8.6 | 0 | 250
500 | 0 | -3.2 | 0 | 500
1000 | 0 | 0 | 0 | 1000
2000 | 0 | 1.2 | -0.2 | 2000
4000 | 0 | 1 | -0.8 | 4000
8000 |  | #VALUE! | #VALUE! | 8000 | Excluded, DIH 10/15/03
16000 |  | -6.6 | -8.5 | 16000
Linear | #VALUE! | - | - | Linear
dBA | - | 6.2515 | - | dBA
dBC | - | - | #VALUE! | dBC
A-wgt | Linear | dBA | dBC | C-wgt
-39.4 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-26.2 |  | #VALUE! | #VALUE! | -0.8
-16.1 | 0 | -16.1 | -0.2 | -0.2
-8.6 | 0 | -8.6 | 0 | 0
-3.2 | 0 | -3.2 | 0 | 0
0 | 0 | 0 | 0 | 0
1.2 | 0 | 1.2 | -0.2 | -0.2
1 | 0 | 1 | -0.8 | -0.8
-1.1 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-6.6 | 0 | -6.6 | -8.5 | -8.5
Overall | #VALUE! | 6.2515 | #VALUE! | Overall
Value | Linear | dBA | dBC | Value

## DbA Calc (4)
Linear, dBA, and dBC Calculations:
June 15, 1995 Version |  |  |  |  | Input O.B. Data Given
Data | Linear | dBA | dBC | No. | Under Linear Column
Freq., Hz. | Input | Calc. | Calc. | Freq., Hz.
31.5 |  | #VALUE! | #VALUE! | 31.5 | Excluded, DIH 10/15/03
63 |  | #VALUE! | #VALUE! | 63
125 | 0 | -16.1 | -0.2 | 125
250 | 0 | -8.6 | 0 | 250
500 | 0 | -3.2 | 0 | 500
1000 | 0 | 0 | 0 | 1000
2000 | 0 | 1.2 | -0.2 | 2000
4000 | 0 | 1 | -0.8 | 4000
8000 |  | #VALUE! | #VALUE! | 8000 | Excluded, DIH 10/15/03
16000 |  | -6.6 | -8.5 | 16000
Linear | #VALUE! | - | - | Linear
dBA | - | 6.2515 | - | dBA
dBC | - | - | #VALUE! | dBC
A-wgt | Linear | dBA | dBC | C-wgt
-39.4 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-26.2 |  | #VALUE! | #VALUE! | -0.8
-16.1 | 0 | -16.1 | -0.2 | -0.2
-8.6 | 0 | -8.6 | 0 | 0
-3.2 | 0 | -3.2 | 0 | 0
0 | 0 | 0 | 0 | 0
1.2 | 0 | 1.2 | -0.2 | -0.2
1 | 0 | 1 | -0.8 | -0.8
-1.1 |  | #VALUE! | #VALUE! | -3 | Excluded, DIH 10/15/03
-6.6 | 0 | -6.6 | -8.5 | -8.5
Overall | #VALUE! | 6.2515 | #VALUE! | Overall
Value | Linear | dBA | dBC | Value